## Terms and Conditions
Terms & Conditions: — pages: 47, 58
No. | Text
1. | The work shall be carried out strictly in conformity with the CPWD General Specification of Electrical Works Part-I (Internal) 2023, and Part-II (External) 2023 for electrical works in force and the Indian Electricity Rule - 1956, as amended upto date.
2. | All the materials, used by the contractor should be got approved from the Engineer-in-Charge or his authorized representative before installation. No payment will be made for any unapproved or sub-standard materials used on the work. Rejected materials should be removed from the site of work within 48 hours, by the contractor.
3. | No T & P shall be issued by the department.
4. | Any damage to the installation/ building during execution of work shall be made good by the contractor at his own cost. Repair work if any, should be done with proper cement and sand ratio and to be match with existing finish.
5. | The rates quoted shall be inclusive of all taxes i.e GST but exclusive of ESI & EPF as it would be reimbursed only (As applicable and eligible) after submitted proper documents of their deposits & to the satisfaction of Engineer-in-charge.
6. | The work shall be carried out in security zone area; hence necessary passes shall have to be arranged by the contractor within Three days award of work for the workers engaged by him.
7. | Lowest Bidder shall submit Police verification of staff/labourers to be employed at site within Five days of the award of work, otherwise panelty of Rs. 500/- per day till submission of Police verification of labourers and start of work. Pending or under process police verification will not be accepted.
8. | The electrical work shall be done strictly in close co-ordination with civil works. No claim for idle labour shall be entertained by the department.
9. | The firm shall submit the type test report for cable & other materials along with all necessary documents like invoice etc. Earth wire to be connected with lugs & thimbles etc.
10. | No item shall be installed having Country of Origin in China.
11. | All termination of electrical cables for sizes higher than 4 Sq. mm shall have to be done with proper thimbles / reducer. Copper thimble / reducer shall be used for copper cable and aluminum ones for Al. cables. Nothing extra shall be paid by the department however end termination of power cables shall be paid extra.
12. | Earth wire in the switch board/DB should be covered with green sleeve for which no extra payment will be made.
13. | Nothing extra shall be paid on account of dismantling the wire, conduit, fittings, fans, DB's & Panel etc. and the same will be deposited to the JE's Store.
14. | All the debris etc. shall be removed from the site of work daily.
15. | Electricity & water shall be supplied by the department free of cost.
16. | The site in much secured important heritage building, so all related bye laws are to be followed.
17. | Normally execution will take place after office hours. & site for the work will be provided one by one.
18. | The watch and ward of the materials installed will be the responsibility of the contractor till handing over to the department on completion of work.
19. | Any accident at site during execution of work to be workman and to the third party shall be responsibility of the contractor and claim if any arises due to such accident shall be on the part of contractor and department shall not entertain any claim in this regard.
20. | Work will be carried out in the occupied building hence labour wastage may be there and no claim in this regard from the contractor shall be entertain by the department.
21. | The site will be provided as and when required.
22. | In order to ensure genuineness of equipment/materials, copy of invoice of each equipment/materials, custom clearance paper in case of imported materials duly authenticated by bidder shall be invariably produce to engineer-in-charge.
23. | The contractor shall submit warranty/ guarantee certificate issued by the manufacturer for 05 (Five) years from the date of completion of work.
24. | The components of the installation shall be suitably designed so as to satisfactorily function under all conditions of operation.
25. | The following documents related to staff/ labour to be deployed at site within 03 days of issued of award letter, failing to submit the below mentioned documents penalty of Rs.1000/- shall be levied. Passport Photo of labour/ staff. (3 Nos. with agency letter pad) a) Valid ID proof of the labour/ staff. b) Police Clearance Certificate not older than 1 year.
26. | It is the responsibility of the contractor that the above documents should be submitted in the office of Assistant Engineer (E), immediately after the award of work, so that entry passes/ token permission can be obtained timely. After getting the entry passes/ token permission from the security officer the contractor should take over the site immediately.
27. | The work must be completed within the stipulated time failing which a recovery for Rs.1000/- per day will be deducted from the contractor's bill.
28. | The payment shall be made minimum amount upto 10 lakhs Or First & Final bill basis and as per subject to the availability of the funds.
29. | The contractor shall use any of the following makes (ISI marked) for use in the work as below after confirming the approval from the Engineer-in-charge as applicable: - a) MS Pipe: Jindal/Jindal Hissar/Tata/Prakash b) Hydrant Valve: New Age/Padmini/Lifeguard c) Butterfly Valve: Sant/Kirloskar/leader d) Sluice Valve: Kirloskar/Sant/Kartar e) NRV: Sant/Kirloskar/Leader f) Y Strainer: Kirloskar/Sant/Kartar g) RRL Hose Pipe: New Age/Padmini/Lifeguard h) First Aid Hose Reel: New Age/Padmini/Lifeguard i) Hose Cabinet: Life Guard/Padmini/New Age/Mild Steel/Valentino j) Signage: Life Guard/Padmini/New Age/Mild Steel/Valentino k) Fire Extinguishers: Ceasefire/ Safex/ Lifeguard/ Flameklog/ Omex/ Agni/ Padmini.
30. | Note :- Failing to submit the following documents, no running and final bill shall be paid to the contractor- M.A.S. Register, Site Order Book, Hindrance register, Attendance sheet of the staff deployed, proof of the payment to the staff, proof of the material procured i/c tax invoice, service report duly singed by JE/AE etc. and any other documents as asked by Engineer-In-Charge.
31. | General Conditions:
32. | 1. All hardware items such as screws, thimbles, connectors, earth/neutral terminals, wires etc. which are essentially required for completing any item as per specifications will be deemed to have been included in the item even when the same have not been specifically mentioned.
33. | 2. All hardware material such as nuts/bolts/screws/washers etc. to be used in the work shall be zinc/cadmium plated iron. The galvanized boxes of modular switch/sockets etc. shall be of the same make as of switch/socket etc.
34. | 3. While laying conduit, suitable minimum number of junction boxes shall be left for pulling the wires. These shall be placed in such a way that the same do not remain noticeable.
35. | 4. Any conduit which is not be wired by the contractor shall be provided with GI fish wire for wiring by some other agency subsequently. Nothing extra shall be paid for the same.
36. | 5. Multi stranded FRLS PVC insulated copper conductor wires are to be used in the work. Termination of multi-stranded conductors shall be done using crimping type copper thimbles at both the ends. Nothing extra shall be paid for the same.
37. | 6. The contractor shall follow the shortest route for circuits, sub-main, point wiring etc.
38. | 7. The connections of switches, sensors, earthing conductors & interconnections cables shall be made by adequate rating thimbles of approved standard makes only and nothing extra on this account shall be paid.
39. | 8. Check nuts shall be provided while terminating the M.S. conduits in switch board boxes for which nothing extra shall be paid.
40. | 9. All distribution boards shall be marked with circuits controlling the rooms/area/SDB controlled.
41. | 10. Material to be used in the work shall be ISI marked. The makes of materials have been indicated in the list of acceptable makes. No other make will be acceptable. The material to be used in the work shall be got approved from the Engineer-in-charge before its use at site. The Engineer-in-charge shall reserve the right to instruct the contractor to remove the material which, in his opinion, is not as per specifications.
42. | 11. While deciding the size of switch boxes for light points/fan point, exhaust fan point items, extra two modules will be provided for each fan point for fixing of regulator(s) (fan regulator is to be provided under different item). Wherever extra modules are available, the same shall be provided with blanking plates without any extra cost.
43. | 12. Modular type switches/sockets/telephone outlets/TV sockets are to be provided wherever indicated in the items. The same shall be of only one make. The modular plates of switches, sockets, telephone & TV sockets etc. shall be in two parts i.e. plates with frames with in quoted rates.
44. | 13. The building shall be provided with false ceiling in various areas. In order to avoid maintenance problem, the contractor will not provide any ceiling rose/connector/looping box above the false ceiling. The point wiring in that case will be extended up to the fitting/fan etc. directly without provisions of any termination arrangement in between. The wire from the end point up to the fixture shall be considered to be included in the point wiring. Nothing extra shall be paid for the same.
45. | 14. Wherever it is not possible to provide rigid conduits, flexible conduit pipe shall be provided for drawing/running the wires. However, such arrangement has to be kept to the barest minimum and only with the prior approval of Engineer-in-charge.
46. | 15. Earthing and all hidden items of work shall be carried out in the presence of the Engineer-in-charge or his authorized representative.
47. | 16. The fan box cover shall be made from 3mm thick phenolic laminated sheet as per CPWD specification.
48. | 17. The contractor shall provide only metallic junction boxes/looping boxes with cover of required sizes even in PVC conduiting and such boxes shall be measured as a part of conduit/wiring without any extra payment.
49. | 18. The metallic junction boxes & looping boxes shall be covered with approved makes of phenolic laminated sheet. For telephone, television & fire alarm system shall be provided at all the floors within scope of work without any extra cost as per requirement & layout approved by Engineer-in-charge.
50. | 19. The firm has to go through the site order book kept with the Junior Engineer (E) regularly and has to sign the same and carryout the instructions recorded therein by various officers of the department.
51. | 20. The quantities of various items may vary from the quantities given in schedule of work. The agency shall bring the various items & materials as per actual requirement at site at the time of execution of work. Excess quantities shall not be accepted & paid by the department.
52. | 21. The ceiling roses wherever required to be provided are included in the scope of work without extra payment and the same shall also be of modular type & of the same make as that of switches & sockets along with earthing provision.
53. | 22. The MCB should be of same make as that of MCB DBs.
54. | 23. The MCB distribution boards shall be factory fabricated in the works of the manufacturer of the MCB's of any of the makes specified and the same shall be duly pre-wired in the works. The board shall be brought to site in ready for installation condition. The MCBs and the MCB distribution board shall be of the same make.
55. | 24. Microprocessor type MCCB should have centrally adjustable overload setting & short circuit setting as per OEM standards. All MCCB should be ICS=ICU.
56. | 25. Suitable crimping tools shall be used for crimping the lugs/thimbles/ferrules. Nothing extra shall be paid on this account.
57. | 26. All the equipment shall be delivered with (i) Manufacturer's test certificate, (ii) Manufacturer's technical catalogues and Installation / Instruction (O&M) manuals.
58. | 27. The work shall be carried out according to approved drawing/details which shall be subsequently issued to the successfully qualified bid bidder for execution, in stages as per instruction of the Engineer-in-Charge who will have the right to change the layout as per requirement at site and the contractor shall not have any claim due to change in layout.
59. | 28. The bad workmanship will not be accepted and defects shall be rectified at contractor's cost to the satisfaction of the Engineer-in-Charge. The program of electrical works is to be coordinated in accordance with the building work.
60. | 29. The contractor or his engineer is bound to sign the site order book as and when required by the Engineer-in-Charge and to comply with the remarks therein.
61. | 30. The contractor has to make his own arrangements for stores and watch & ward. No extra claim for this will be entertained.
62. | 31. The wiring and conduit route shall be marked by the contractor in the drawing first, and shall be got approved from the Engineer-in-charge.
63. | 32. The connection inter connection, earthing and inter earthing shall be done by the contractor where required and nothing extra shall be paid on this account.
64. | 33. All the sub main and circuits wiring includes loose wire for connections inside switch boxes and MCB DBs. No payment for these loose wires shall be made.
65. | 34. All PVC/ MS conduits accessories shall be of the same make as conduits and shall be ISI marked. The conduits shall be terminated as switch boxes/metallic junction boxes with suitable glands/check nuts.
66. | 35. The contractor shall take all safety precautions to avoid accidents by exhibiting caution boards, red flags, red lights and by providing necessary barriers and all other measures required from time to time. The contractor shall be responsible for all damages and accidents due to negligence on his part.
67. | 36. The contractor shall give due notices to Municipality, Police and/or other authorities that may be required under the law/rules under force and obtain all requisite permissions/licenses for temporary obstructions/enclosures and pay all charges which maybe liable on account of.
68. | 37. The contractor shall leave such recesses, holes, openings, etc., as may be required for the electric, air-conditioning and other related works. (For this purpose, any required inserts, sleeves, brackets, conduits, base plates, insert plates, clamps etc. shall be arranged by the contractor and fix the same at the time of casting of concrete, stone work & brick work, if required, and nothing extra shall be payable on this account.
69. | 38. No tools and plants including special T&P etc. shall be supplied by the department and the contractor will have to make his own arrangements at his expenses.
70. | 39. All materials shall be got checked & approved by the Engineer-in-charge on receipt of the same at site before use and rejected material is to be removed from the site immediately.
71. | 40. No foreign exchange shall be made available by the department for the purchase of equipment, plants, machinery, materials of any kind or any other items required to be carried out in execution of work.
72. | 41. The contractor shall carry out his work, so as not to interfere with or hinder the progress or completion of the work being performed by other contractor(s) or by the Engineer-in-charge and shall as far as possible arrange his work and shall place and dispose of the materials being used or removed, so as not to interfere with the operations of other contractors, or he shall arrange his work with that of the others in an acceptable and coordinated manner and shall perform it in proper sequence to the entire satisfaction of Engineer-in-charge.
73. | 42. All items which are not covered while carrying out electrical work shall be removed and shall be cleared by the contractors as soon as the work is completed.
74. | 43. The contractor shall give the Engineer-in-charge in every fortnight, a progress report of the work done during the previous fortnight. The progress of work will be reviewed periodically by the Engineer-in-charge with the contractor and shortfalls, if any, sorted out. The contractor shall thereupon take such action as may be necessary to bring back his work to schedule without any additional cost to the department.
75. | 44. It shall be responsibility of the main contractor to sort out any dispute involved with the associated contractor without any time and cost overrun to the department. The main contractor shall be solely responsible for settling the dispute/litigation arising out of his agreement with the associate contractor. The contractor shall ensure that the work shall not suffer on this account.
76. | 45. The contractor shall quote his rates considering the specifications, terms & conditions and particular specifications and special conditions etc. and nothing extra shall be payable whatsoever unless otherwise specified.
77. | 46. The main contractor shall be responsible for coordinating the activities of all works and essential progress of works as per milestone and laid down program.
78. | 47. The contractor shall be responsible for the watch and ward of the site/property/material provided by him and materials issued by the department against pilferage and breakage during the period of execution and thereafter till the work is completed and physically handed over to the department.
79. | 48. Samples of all materials, fittings and other materials/articles required for execution of the work shall be got approved from the Engineer-in-charge. Materials/articles manufactured by the firms of repute as indicated in tender documents and approved by the Engineer-in-charge shall only be used.
80. | 49. The contractor shall ensure quality construction in a planned and time bound manner. Any sub-standard material or work beyond set out tolerance limits shall be summarily rejected by the Engineer-in-charge.
81. | 50. Even ISI marked materials shall be subjected to quality test at the discretion of the Engineer-in-Charge besides testing of other materials as per the specifications described for the item/material. Whenever ISI marked materials are brought to the site of work; the contractor shall, if required by the Engineer-in-Charge, furnish manufacturers test certificates to establish that the materials procured by the contractor for incorporation in the work satisfy the provisions of IS codes relevant to the material and/or the work done.
82. | 51. The firm shall use only electrically operated chase cutting machine for cutting the chases in the wall for recessed conduit wiring.
83. | 52. The contractor will have to make his own arrangement for storage of materials. No storage space shall be provided by department.
84. | 53. The contractor will have to ensure that the skilled labour i.e. wireman etc., Engaged in the execution of the work must possess valid electrical license, otherwise he will not be permitted to execute the work.
85. | 54. The associate contractors executing the electrical works must possess the valid electrical contractor license otherwise they will not be permitted to execute the electrical works.
86. | 55. The contractor shall be responsible for removal of all defects in the work during the guarantee/warranty period. The department shall carry out routine maintenance only. However, if any failure is noticed during this period which is attributable to poor quality of material and bad workmanship, the contractor will be required to rectify the same at his own cost, failure of which the department will be at liberty to get the defects rectified at the risk & cost of the contractor. The contractor will also be required to carry out his own inspection/testing during the guarantee/warranty period and attend to any defect taking place during this period.
87. | 56. The contractor has to intimate his authorized representative, who will be receiving instructions in his absence. The contractor /his authorized representative is bound to sign the site order book as and when required by the Engineer-in-charge and to comply with the instructions therein.
88. | 57. Suitable back plates providing for fixing the wall brackets and ceiling flush fittings shall be supplied by the contractor free of cost.
89. | 58. It shall be responsibility of contractor to provide polythene/PVC plastic cover for all SDBs/meter boards/feeder pillars/panels etc. so as to protect them from wear & tear/damage during execution stage. Contractor shall provide the covers for the materials if any being supplied departmentally also. Nothing extra shall be paid on this account.
90. | 59. Contractor is fully responsible for any kind of damage to the LT/HT cable during execution of work. No joints shall be allowed if the cable is damaged. Contractor has to replace the full length at his own cost.
91. | 60. A suitable brass/tinned copper neutral link shall be fixed at suitable place in the Metallicoutlet boxes of all sizes to terminate neutral wire properly. Nothing extra shall be paid on this account
92. | 61. Colour coding shall have to be adopted in the wiring system as per specification.
93. | 62. Suitable crimping tools shall be used for crimping the lugs/thimbles/ferrules. Nothing extra shall be paid on this account. The lugs/thimbles/ferrules pressed by conventional/ordinary pliers shall not be accepted.
94. | 63. A suitable brass/tinned copper neutral link shall be fixed at suitable place in the Metallic outlet boxes of all sizes to terminate neutral wire properly. Nothing extra shall be paid on this account.
95. | 64. An earth termination with earth stud of brass/tinned copper i/c 2 No. metallic washers or suitable earth bar of Brass/tinned copper with tinned copper thimbles/ferrules/lugs should be suitably fixed at suitable place in the Metallic outlet box for termination of protective earth conductor. Nothing extra shall be paid on this account.
96. | 65. In the outlet boxes, phase from one switch to other switch shall be looped with suitable size of solid copper conductor. Nothing extra shall be paid on this account. Stranded conductor shall not be accepted.
97. | 66. Only required number of knockouts should be removed from Metallic outlet boxes for entry of conduits. If more than required number of knockouts are removed, the Metallic outlet box shall not be accepted.
98. | 67. Separate G.I. boxes shall be used for staircase light switches and bell push. Nothing extra shall be paid on this account.
99. | 68. Metal sheath of Co-axial T. V. cable shall be terminated using 'U' shape thimble/lugs/ferrules. Nothing extra shall be paid on this account.
100. | 69. To facilitate drawing of wires 16/18 SWG GI fish wire be provided along with laying of recessed conduit. Nothing extra shall be paid on this account.
101. | 70. Cable connection to switch gear is deemed to be included in the item of end termination. No extra payment shall be made for that.
102. | 71. The contractor is advised to visit the site of work to have an idea of the execution of the work; failure to do so shall not absolve their responsibility to do the work as specified in agreement.
103. | 72. The overall system shall be designed in such that if any monitoring system fails Data Center shall still be functional.
104. | 73. A continuous cooling system to be designed to provide a stable thermal environment for the critical IT equipment without any interruption meeting ASHRAE standards.
105. | 74. The design of the system should be such that it should be fault tolerant site infrastructure covering dual power for all IT equipment, complimentary system and distribution paths must be physically isolated from each other.
106. | 75. The successful bidder has to obtained all statuary approval including PESCO (Petroleum & safety organization) licence for fuel storage above 2000 ltrs and its subsequent renewal before the expiry of defect liability period.
107. | 76. Rates: 76.1 The work shall be treated as on works contract basis and the rates tendered shall be for complete items of work (except the materials, if any, stipulated for supply by the department) inclusive of all taxes (including works contract tax, if any), duties, and levies etc. and all charges for items contingent to the work, such as packing, forwarding, insurance, freight and delivery at site for the materials to be supplied by the contractor, watch and ward of all materials (including those supplied by the department, if any) for the work at site etc.
107a. | 76.2 Prices quoted shall be firm.
108. | 77. Taxes and Duties: 77.1 Rates are inclusive of GST and all other Taxes, duties, levies and royalties and nothing extra shall be payable to the contractor on account of this. 77.2 The GST at source shall be deducted from the bills of the contractor as applicable in at the time of payments.
109. | 78. Completeness of Tender: All sundry fittings, assemblies, accessories, hardware items, foundation bolts, termination lugs for electrical connections as required, and all other sundry items which are useful and necessary for proper assembly and efficient working of the various components of the work shall be deemed to have been included in the tender, whether such items are specifically mentioned in the tender documents or not.
110. | 79. Works to be done by the contractor: Unless and otherwise mentioned in the tender documents, the following works shall be done by the contractor, and therefore their cost shall be deemed to be included in their tendered cost :- (i) Foundations for equipment and components where required, including foundations bolts. (ii) Cutting and making good all damages caused during installation and restoring the same to their original finish. (iii) Sealing of all floor openings provided by him for pipes and cables, from fire safety point of view, after laying of the same. (iv) Painting at site of all exposed metal surfaces of the installation other than prepainted items like fittings, fans, switchgear/distribution gear items, cubical switchboard etc. Damages to finished surfaces of these items while handling and erection, shall however be rectified to the satisfaction of the Engineer-in-Charge. (v) Testing and commissioning of completed installation. (vi) Storage space for all equipment, components and materials for the work.
111. | 80. Storage and Custody of Materials: The contractor has to make his own arrangement for the storage of the material at site & necessary watch and ward of the electrical installation during the execution of work till the same is handed over to the department. No extra payment will be made on this account. The storage space shall however be arranged by the department at site, if available. The main contractor shall arrange for proper storage of the electrical fans and fittings at site and that double lock system shall be arranged for the fans and fittings after receipt at site until the time they are taken for installation. The contractor shall however be responsible for proper storage and safe custody of the same till their installation and handing over to the department.
112. | 81. Electric Power Supply and Water Supply: Power and water supply will be arranged by the contractor at the site for installation purpose. However, for final testing purpose after complete installation of the electrical items, electricity supply will be made available free of cost to the contractor or the Contractor shall make his own arrangement by deploying necessary DG Sets. Contractor will take due care to ensure safety of electrical installation during execution of work.
113. | 82. Tools for handling and Erecting: All tools and tackles required for handling of equipment and materials at site of work as well as for their assembly and erection and also necessary test instruments shall be the responsibility of the contractor.
114. | 83. Payment Terms: Payment shall be made as per the relevant clauses of form PWD -EPC forming part of the tender documents.
115. | 84. Co-ordination with other agencies: The contractor shall co-ordinate with all other agencies involved in the building work so that the building work is not hampered due to delay in his work. Recessed conduit and other works, which directly affect the progress of building work, should be given priority.
116. | 85. Care of buildings: Care shall be taken by the contractor to avoid damage to the building during execution of his part of the work. He shall be responsible for repairing all damages and restoring the same to their original finish at his cost. He shall also remove, at his costs, all unwanted and waste materials arising out of his work, from the site.
117. | 86. Structural Alterations to Buildings: (i) No structural member in the building shall be damaged/altered, without prior approval from the competent authority through the Engineer-n-charge. (ii) Structural provisions like openings, cutouts, if any, provided by the department for the work, shall be used. Where these required modifications, or fresh provisions are required to be made, such contingent works shall be carried out by the contract at his cost. (iii) All such openings in floors provided by the department shall be closed by the contractor after installing the cables/conduits/rising mains etc. as the case may be, by any suitable means as approved by the Engineer-in-charge without any extra payment. (iv) All chases required in connection with the electrical works shall be provided and filled by the contractor at his own cost to the original architectural finish of the buildings.
118. | 87. Addition to an installation: Any addition, temporary or permanent, to the existing/ Proposed electrical installation shall not be made without a properly worked out scheme/design by a qualified Electrical Engineer to ensure that such addition does not lead to overloading, safety violation of the existing/ Proposed system.
119. | 88. Work in occupied buildings: (i) When work is executed in occupied buildings, there would be minimum of inconvenience to the occupants. The work shall be programmed in consultation with the Engineer-in-charge and the occupying department. If so required, the work may have to be done even before and after the office hours. (ii) The contractor shall be responsible to abide by the regulations or restrictions set in regard to entry into, and movement within the premises. (iii) The contractor shall not tamper with any of the existing installations including their switching operations or connections there to without specific approval from the Engineer-in-Charge.
120. | 89. Drawings: (i) The work shall be carried out in accordance with the drawings and the tender documents and also in accordance with modification thereto from time to time as approved by the Engineer-in-charge. (ii) All wiring diagrams shall be deemed to be 'Drawings' within the meaning of the term as used in Clause 11 of the conditions of contract (PWD 7 or PWD 8). They shall indicate the main switch board, the distribution boards (with circuit numbers controlled by them), the runs of various mains and sub mains and the position of all points with their controls. (iii) After award of the work, the firm will be required to submit the drawings for the proposed work including layout plan, conduit routes showing location of points and height etc. Work will be carried out as per the approved drawings before start of work.
121. | 90. Conformity to IE Act, IE Rules, and standards: 1.2. All electrical works shall be carried out in accordance with the provisions of Indian Electricity Act, 1910 and Indian Electricity Rules, 1956 amended up to date (Date of call of tender unless specified otherwise). List of rules of particular importance to electrical installations under these General Specifications is given in Appendix C for reference.
122. | 91. General requirements of components: 1.3. Quality of material: All materials and equipment supplied by the contractor shall be new. They shall be of such design, size and materials as to satisfactorily function under the rated conditions of operation and to withstand the environmental conditions at site.
123. | 92. Inspection of materials and equipment: 92.1 Materials and equipment to be used in the work shall be inspected by Engineer-in-charge or his representative or both officers as required. Such inspection will be of following categories: (i) Inspection of materials / equipment to be witnessed at the Manufacturer's premises in accordance with relevant BIS /Agreement Inspection Procedure. (ii) To receive materials at site with Manufacturer's Test Certificate(s) (iii) To inspect materials at the authorized dealer's go downs to ensure delivery of genuine materials at site. (iv) To receive materials after physical inspection at site.
124. | 92.2 Adequate care to ensure that only tested and genuine materials of proper quality are used in work shall be ensured by firm. The firm shall ensure that: (i) Material will be ordered & delivered at site only with the prior approval of the department to ensure timely delivery. (ii) As and when the order is placed for the fittings/ fixtures, cables, switchgears, poles, rising main, other main items etc., its copy shall be endorsed to the CPWD Engineer-in-charge. (iii) The firm will be required to procure material like exhaust fans, MCB's & DB's, switches & sockets, wires & cables, conduits and switchgears etc directly from the manufacturer/ authorized dealers to ensure genuineness & quality and as per the approved makes only. Proof in this regard shall be submitted by the contractor before installation at site to the department. (iv) Inspection at factory or at goodown of the manufacturer, as required, shall be arranged by the firm for a mutually agreed date. Certificate for genuineness of the fittings shall have to provided duly signed by the manufacturer's officer not below the rank of Regional Manager. (v) Delivery of material shall be taken up only with the consent of department, after clearance of the material. (vi) Department shall reserve the right to waive inspection in lieu of suitable test certificate, at its discretion. NOTE: The boarding lodging and travelling charges for such inspection shall be borne by the department on first instance, in case of failure of the test / non-satisfaction of the test by the department all such expenses shall have to borne by the agency for sub-sequent visit/inspection.
125. | 92.3 Similarly, for fabricated equipment, the contractor will first submit dimensional detailed drawings for approval before fabrication is taken up in the factory. Suitable stage inspection at factory also will be made to ensure proper use of materials, workmanship and quality control.
126. | 93. Ratings of components: 93.1 All components in a wiring installation shall be of appropriate ratings of voltage, current and frequency, as required at the respective sections of the electrical installations in which they are used. 93.2 All conductors, switches and accessories shall be of such size as to be capable of carrying the maximum current, which will normally flow through them, without their respective ratings being exceeded.
127. | 94. Conformity to standards: 94.1 All components shall confirm to relevant Indian Standard Specifications wherever existing. Materials with ISI certification mark shall be preferred. 94.2 Relevant Indian Standards including amendments or revisions thereof up to the date of tender acceptance shall be applicable in the respective contracts for respective items, firm to ensure its compliance.
128. | 95. Inter-changeability: Similar parts of all switches, lamp holders, distribution fuse boards, Switch gears, ceiling roses, brackets, pendants, fans and all other fittings of the same type shall be interchangeable in each installation.
129. | 96. Workmanship: 96.1 Good workmanship is an essential requirement to be complied with. The entire work of manufacture/fabrication, assembly and installation shall confirm to sound engineering practice. 96.2 Proper supervision/skilled workmen: The contractor shall be a licensed electrical contractor of appropriate class suitable for execution of the electrical work. He shall engage suitably skilled/licensed workmen of various categories for execution of work supervised by supervisors / Engineer of appropriate qualification and experience to ensure proper execution of work. They will carry out instruction of Engineer-in-charge and other senior officers of the Department during the progress of work. 96.3 Use of quality materials: Only quality materials of reputed make as specified in the tender will be used in work. 96.4 Fabrication in reputed workshop: Switch boards and LT panels shall be fabricated in a factory/workshop having modern facilities like quality fabrication, seven tank process, powder/epoxy paint plant, proper testing facilities, manned by qualified technical personnel. These shall be as per make / item approved.
130. | 97. Testing: All testes prescribed in this General Specification, to be done before, during and after installation, shall be carried out, and the test results shall be submitted to the Engineer-incharge in prescribed Performa, forming part of the Completion Certificate.
131. | 98. Commissioning on completion: After the work is completed, it shall be ensured that the installation is tested and commissioned.
132. | 99. Completion plan and completion certificate: 99.1 For all works completion certificate after completion of work shall be submitted to the Engineer-in-charge. 99.2 Completion plan drawn to a suitable scale in A2 Sheet indicating the following, and three copies of the same shall also be submitted. (i) General layout of the building. (ii) Locations of main switchboard and distribution boards, indicating the circuit numbers controlled by them. (iii) Position of all points and their controls. (iv) Types of fittings, viz. fluorescent, pendants, brackets, bulk head, fans, exhaust fans etc. (v) Name of work, job number, tender reference, actual date of completion, names of Division/ Sub-division and name of the firm who executed the work with their signature. (vi) Cable layout showing general distribution diagram along with position of cable joints, if any.
133. | 100. Guarantees The installation will be handed over to the department after necessary testing and commissioning. The installation will be guaranteed against any defective design/workmanship. Similarly, the materials supplied by the contractor will be guaranteed against any manufacturing defect, inferior quality. The guarantee period will be for a period of 36 months from the date of handing over to the department. Installation/ equipment or components thereof shall be rectified/ repaired to the satisfaction of the Engineer-in-charge. The firm will be required to submit guarantee of material from the manufacturer to the department.
101. | The tenderer is advised to read and examine the tender documents for the work and the set of drawings in the tender document and also available in office of Engineer-in-charge. He should himself inspect and examine the site and its surroundings before submitting his tender.
102. | Separate conditions & specification and scope are included in this tender for each of the subhead. The contractor shall quote the amount/rates lump-sum in figure/percentage accurately in schedule of financial quote, as prescribed there.
103. | The contractor(s) shall submit a detailed program of execution in accordance with the master programme/milestone within ten days from the date of issue of award letter.
104. | All the E&M Items shall be brought at site only after the approval of TDS & physical sample of the item/equipment and same shall be preserved at site lab/sample room. The Test Report from OEM/Third Party/Both for each/any E&M item/equipment can be sought by the Engineer-in-Charge.
105. | The payment for the tests shall be borne by agency, and no reimbursement shall be made by the department. If the agency fails to submit the test reports from OEM/Third Party/Both for each/any E&M item/equipment as sought by the Engineer-in-Charge, then the department will get all the required tests done and the amount paid to the test agency by the department will be recovered from the contractor bill.
106. | All works have to be executed as per specifications provided in the bid document, CPWD Specifications, National building Code 2016 (in case of difference, if any, stringent/higher specification of the two shall be followed) and ECBC 2017 Code. In absence of CPWD Specifications, IS Codes, National Building Code 2016 sound engineering practices shall be adopted as per order of precedence defined in the contract.

## Acceptable Make
Acceptable Make — pages: 48, 53
No. | Text
a) | MS Pipe: Jindal/Jindal Hissar/Tata/Prakash
b) | Hydrant Valve: New Age/Padmini/Lifeguard
c) | Butterfly Valve: Sant/Kirloskar/leader
d) | Sluice Valve: Kirloskar/Sant/Kartar
e) | NRV: Sant/Kirloskar/Leader
f) | Y Strainer: Kirloskar/Sant/Kartar
g) | RRL Hose Pipe: New Age/Padmini/Lifeguard
h) | First Aid Hose Reel: New Age/Padmini/Lifeguard
i) | Hose Cabinet: Life Guard/Padmini/New Age/Mild Steel/Valentino
j) | Signage: Life Guard/Padmini/New Age/Mild Steel/Valentino
k) | Fire Extinguishers: Ceasefire/ Safex/ Lifeguard/ Flameklog/ Omex/ Agni/ Padmini

## Documents to Upload
LIST OF DOCUMENTS FOR NON-CPWD REG. SPECIALIZED AGENCIES/MANUFACTURERS/OEM — pages: 6, 7
No. | Text
1. | Earnest Money Deposit: Banker's Cheque of a Commercial Bank / Account Payee Demand Draft of a Commercial Bank / Fixed Deposit Receipt (FDR) of a Commercial Bank / Insurance Surety Bonds / Bank Guarantee including e- Bank Guarantee (for balance amount as prescribed) from a Commercial Bank against EMD.
2. | Copy of EMD receipt [Form F]: Copy of receipt for deposition of original EMD to division office of any EE, CPWD. Scanned copy of original Bank Guarantee including e-Bank Guarantee of any commercial Bank against EMD. (Note :- EMD is required to deposit in the office of Executive Engineer (E), DED-101, CPWD, Gate No. 6, North Block, New Delhi who is inviting bid or Division office of any Executive Engineer, CPWD within the period of bid submission).
3. | Certificate of financial turn over from Chartered Accountant (Form - "A"): Certificate of Financial Turnover including Profit / Loss duly audited by Charted Accountant for the last 3 financial years ending 31st March 2024, as per Form A.
4. | Banker's Certificate / Net Worth Certificate (Form B/ B-1) Copy of Banker's Certificate or Net worth certificate (on the format prescribed in Form B or B1 as applicable).
5. | Certificates of Work Experience as per Form C: Details of Eligible Similar Nature of Works Completed During the Last Seven Years Ending Previous Day of Last Day of Submission of Tenders. [List of eligible similar nature of works completed during the last seven years ending last day of month previous to the one in which bids are invited including extended date, if any, in Form - C. If private works shown in support of eligibility, then certified copy of Tax Deducted at Source (TDS) certificate (Form 16A & 26A) shall be submitted along with experience certificate and the TDS amount shall tally with the actual amount of work done. Otherwise, the amount that tally with the TDS shall only be considered for eligibility.] NOTE: * Only eligible similar work fulfilling the eligibility criteria as per NIT shall be uploaded.
6. | Work Experience certificate of Completed works mentioned in Form-C, certified by owner department (Form-G).
7. | Project under execution as per Form C1.
8. | Bidding capacity as per Form C3.
9. | Affidavit: Affidavit for eligible similar works not having been executed on back-to-back basis (Form- H).
10. | GST Registration GST Registration certificate AND/OR Undertaking (Form "M"): GST registration certificate of the state where the work is to executed, if already obtained by the bidder. If the bidder has not obtained GST registration as applicable, then in such a case the bidder shall upload the following undertaking with the bid document. "If work is awarded to me, I/We shall obtain registration certificate as applicable within one month from date of receipt of award letter or before payment of 1st R.A. bill whichever is earlier, falling which, I/We shall be responsible for any delay in payments which will be due towards me on account of the work executed and/ or for any action taken by CPWD or GST department in this regard".
11. | PAN Card: Copy of the PAN of the Bidder.
12. | Undertaking as per Annexure D1.
13. | ERP training certificate or Undertaking (Annexure "D2"): Copy of valid ERP training certificate OR Undertaking, that if we become first lowest in tender, then either myself or our authorized representative will take compulsory ERP training through any of the CPWD Regional Training Institutes (RTIs) at Delhi, Mumbai, Chennai and Kolkata, National CPWD Academy (NCA) Ghaziabad, Training arranged by graduates of ERP "Train the Trainers Programme" conducted by NCA, Ghaziabad or through any other special training arranged by ERP Unit of CPWD within two months from the date of issue of Intent Letter.
14. | Undertaking as per Annexure-D3.
15. | Valid Electrical Licence or Undertaking of association: Copy of Valid Electrical Licence OR Undertaking as per Annexure-D4.
16. | Undertaking as per Annexure-D9.
17. | Any other document as specified in bid document.
Notes
* | 1. All the documents shall be scanned from the original document.
* | 2. All the documents shall be signed and stamp by the contractor.
* | 3. The documents shall be strictly as per the format given in the NIT.
* | 4. All the documents shall be duly indexed and page numbered (as per Annexure D).
* | 5. No cutting and overwriting shall be accepted.
* | 6. Only one pdf of all documents may be uploaded.
* | 7. Irrelevant and undesirable shall not be uploaded.
* | 8. The Lowest Bidder is required to produce original document on or before or at the time of submission of Performance guarantee Money which are uploaded by the bidder at the time of bid submission otherwise Performance guarantee Money shall not be accepted and EMD shall be forfeited.
LIST OF DOCUMENTS FOR CPWD REG. CONTRACTORS — pages: 8, 9
No. | Text
1. | Earnest Money Deposit: Banker's Cheque of a Commercial Bank / Account Payee Demand Draft of a Commercial Bank / Fixed Deposit Receipt (FDR) of a Commercial Bank / Insurance Surety Bonds / Bank Guarantee including e- Bank Guarantee (for balance amount as prescribed) from a Commercial Bank against EMD.
2. | Copy of EMD receipt [Form F]: Copy of receipt for deposition of original EMD to division office of any EE, CPWD. Scanned copy of original Bank Guarantee including e-Bank Guarantee of any commercial Bank against EMD. (Note :- EMD is required to deposit in the office of Executive Engineer(E), DED-101, CPWD, Gate No. 6, North Block, New Delhi who is inviting bid or Division office of any Executive Engineer, CPWD within the period of bid submission).
3. | Valid Enlistment Order: Contractor of the Composite Category in CPWD in appropriate Class valid on the last date of submission of bid.
4. | Affidavit: Affidavit for eligible similar works not having been executed on back-to-back basis (Form- H).
5. | GST Registration certificate AND/OR Undertaking (Form "M"): GST registration certificate of the state where the work is to executed, if already obtained by the bidder. If the bidder has not obtained GST registration as applicable, then in such a case the bidder shall upload the following undertaking with the bid document. "If work is awarded to me, I/We shall obtain registration certificate as applicable within one month from date of receipt of award letter or before payment of 1st R.A. bill whichever is earlier, falling which, I/We shall be responsible for any delay in payments which will be due towards me on account of the work executed and/ or for any action taken by CPWD or GST department in this regard".
6. | PAN Card: Copy of the PAN of the Bidder.
7. | Undertaking as per Annexure D1.
8. | Bidding capacity as per Form C3.
9. | ERP training certificate.
10. | Undertaking as per Annexure D3.
11. | Valid Electrical Licence or Undertaking of association: Copy of Valid Electrical Licence OR Undertaking as per Annexure-D4.
12. | Undertaking as per Annexure-D9.
13. | Any other document as specified in bid document.
Notes
* | 1. All the documents shall be scanned from the original document.
* | 2. All the documents shall be signed and stamp by the contractor.
* | 3. The documents shall be strictly as per the format given in the NIT.
* | 4. All the documents shall be duly indexed and page numbered (as per Annexure D).
* | 5. No cutting and overwriting shall be accepted.
* | 6. Only one pdf of all documents may be uploaded.
* | 7. Irrelevant and undesirable shall not be uploaded.
* | 8. The Lowest Bidder is required to produce original document on or before or at the time of submission of Performance guarantee Money which are uploaded by the bidder at the time of bid submission otherwise Performance guarantee Money shall not be accepted and EMD shall be forfeited.